Number  6	October 31, 1995

Configuring the A-B Ethernet Direct Using Microsoft TCP/IP 3.11b  by Neal Hatton

This shows a “real world” example of configuring the Wonderware® Allen-Bradley Ethernet Direct (ABTCP) DDE server with Microsoft Windows for Workgroups (WFW) and Microsoft TCP/IP version 3.11b.  Your system may not be exactly as what is shown in this example, but this example is a good starting point for a configuration that works.

Note:  Wonderware Technical Support recommends that you use the latest version of Microsoft TCP/IP which is version 3.11b.  You can get TCP/IP version 3.11b from the Microsoft Download Service (phone (206) 936-6735).

## Step 1

Begin to install Microsoft TCP/IP version 3.11b by entering the Windows Program Manager and double-click the Network Setup icon in the Network Program Group:

## Step 2

The Network Setup dialog box should appear:

Highlight “Microsoft TCP/IP-32 3.11b” and click the Drivers button.

## Step 3

The Network Drivers dialog box should then appear:

Highlight “Microsoft TCP/IP-32 3.11b” and click the Setup button.

## Step 4

The Microsoft TCP/IP Configuration dialog box should then appear:

Select the appropriate Adapter (example: 3Com EtherLink III) and enter your IP address (example: 123.123.123.123) and the Subnet Mask (example: 255.255.255.1).  Then, click OK.  Note that these are the only required entries and that you may leave the remaining fields blank (that is, the Default Gateway and the Primary and Secondary WINS Server).

## Step 5

Verify the configuration of the TCP/IP network driver by clicking the Advanced button on the Microsoft TCP/IP Configuration dialog box that is shown in step 4.  This brings up the Advanced Microsoft TCP/IP Configuration dialog box:

Make sure that the only entries listed are the IP Address and the Subnet Mask which was entered in step 4.  That is, the Windows Networking Parameters checkboxes and the Enable WINS Proxy Agent checkbox should all be unchecked.  Click the OK button.

## Step 6

Click the DNS button on the Microsoft TCP/IP Configuration dialog box in step 4 which brings up the Microsoft TCP/IP - Connectivity Configuration dialog box:

Enter the Host Name of your computer (example: wondernode).  Do not enter the host name of the PLC.  Click OK.  Then, exit the Microsoft TCP/IP network setup by closing the Network Drivers dialog box and clicking OK on the Network Setup dialog box.

## Step 7

Use a text editor like Notepad and create a text file called HOSTS.TXT under the \WINDOWS directory.  Then rename the file to HOSTS (with no file extension).

Note:  If you are using Win 95 or Windows for Workgroups and you need to view or edit the HOSTS file using the text editor, you will first need to rename the file to HOSTS.TXT.  When you are finished editing or viewing the file, be sure to rename the file to HOSTS (with no file extension).

Enter the IP address and host name for each PLC that you want to connect to.  Here is an example of a typical HOSTS file:

123.123.123.1   PLC540E

123.123.123.2   PLC520E

123.123.123.3   PYRAMID

123.123.123.4   PLC560E

The left column lists the IP addresses of the PLCs and the right column lists the corresponding host names of the PLCs.  Remember that your HOSTS file will contain different IP addresses and host names than what is shown above.

## Step 8

Configure the ABTCP DDE server by starting up the ABTCP server:

Choose Topic Definition from the ABTCP Configuration menu.  The A-B Ethernet Direct Topic Definition dialog box should appear:

Enter an arbitrary name for the DDE Topic Name and choose the appropriate PLC Host Name.  Wonderware Technical Support recommends that you initially choose Local for the PLC Addressing since this is the simplest way to connect to the PLC.  Consult the Wonderware ABTCP user’s guide for information on the remaining options on this dialog box.

Click the OK button, then exit the ABTCP server.

## Step 9

Test the TCP/IP configuration by restarting Microsoft Windows and go to a DOS prompt.  Use the PING utility and “ping” the PLC to which you want to communicate.  (Make sure that you “ping” the PLC by its host name and not by its IP address.)

Here is an example of a successful PING operation:

> PING Node_Name

Reply From 123.123.123.123

bytes=xx time<xxms TTL = xx  	(This may repeat more than one time.)

Where Node_Name is the host name of the PLC, xx is some number, and 123.123.123.123 is the IP address of the PLC.  (Note that the format of the PING reply may vary, depending on the PING utility that you use.)

Here is an example of an unsuccessful PING operation:

> PING Node_Name

Bad IP Address nodename

This either means the Node_Name was not defined in the HOSTS file, the HOSTS file is missing, or the HOSTS file is some name other than HOSTS.

Here is another example of an unsuccessful PING operation:

> PING Node_Name

Request Timed Out

This means the Node_Name is defined in HOSTS file, but there is a network problem.  You should check things such as the network cabling, the computer and the PLC, the network terminations and the network card.

## Step 10

If the PING operation was successful, then you are ready to communicate to the PLC using the Wonderware ABTCP DDE server.  Complete the test by finding a suitable client (such as Microsoft Excel or InTouch) and see if you can bring in one register from the PLC.

The Technical Support Tech Note is published occasionally by the Wonderware Technical Support group.  Editor: Mari Fujii;  Manager, Technical Support: Don Mauldin;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92718.

There is also technical information on the Wonderware software products on Wonderware’s Bulletin Board Service (BBS) at (714) 727-0726 and on the Wonderware Comprehensive Support CD (CSCD) that is issued once a quarter.  Call Wonderware Technical Support at (714) 727-3299 (or E-mail to support@wonderware.com) for more information.

Copyright 1995 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

October 31, 1995  Number 6