Number  13	April 19, 1996

Square D Network Routing Explained  by Terry Butterfield

This Tech Note applies to the Wonderware® Square D SY/ENET, SY/MAX Point-to-Point, and SY/LINK DDE I/O Servers.  All three of these Square D servers have the following field displayed on the DDE Server’s Topic dialog box:

For many users, what is supposed to be entered in this field is a mystery.  This Tech Note was written to take some of the mystery out of Square D network routing and to define some of the rules of network addressing.

Note  This Tech Note applies to the Wonderware Square D DDE Servers only.  Other Square D vendor software (for example, the Square D programming software) may be able to perform network routing that is different than what the Wonderware Square D servers will do.

# Overview of Square D Routing

Routing provides a way to address from a Source node to a Destination node.  This route must include all intermediate points or Bridges.  For example, here is a typical network route which is illustrated in Figure 1 on the last page:

Source: Personal computer (PC) on Net “A”

Bridge: PLC Model 400 on Net “A”

Destination: PLC Model 400 on Net “B”

Referencing Figure 1, the route address for this example would be:  4, 123, 23.

The simplest route would be between two points (Point-to-Point).  But, the confusion begins when the network becomes more complex with additional PCs and PLCs.  Square D allows you a maximum of seven routing numbers for the Source and Destination and a maximum of five Bridges.

## Type of Hardware Used

### Network Interface Module (NIM)

There are DIP switches in the Network Interface Module (NIM) which set the following items:

- Network speed

- COM port speed (typically 9600 baud is the maximum)

- Net-to-Net / SY/MAX

- Network size (31 or 100)

Within a network, a NIM address can be used only once.  To function as a Bridge, two NIMs (each on a separate network) must have the same address and be connected through the same communication port (that is, COM0 or COM1).  Figure 1 shows three networks, Net “A”, “B”, and “C” in which NIM address 23 is the Bridge between Net “A” and “B”, and NIM address 28 is the Bridge between Net “B” and “C”.

SY/LINK Card

The SY/LINK card is essentially a NIM that slides into the PC.  The SY/LINK card has two connections or ports.   Port 0 (zero) connects to a SY/NET network.  Port 1 is for the RS-422 multi-drop applications (as shown in Figure 1 on the PC in Net “A”).

The SY/LINK card’s address is defined by selecting Configure in the Square D server’s menu.  The address can range from 0 to 99.  Though the SY/LINK card is basically a NIM for the PC, it is different in that it contains no thumbwheel or switch settings.  This means the card can be used as a Source or a Destination only, never as a Bridge!

Note  Wonderware® InTouch™ does not use a software interrupt.  If a SY/LINK card is being used by the Square D programming software, the card will be initialized at a certain software interrupt.  This interrupt stays active, even after you exit the Square D software.  Thus, you must turn the PC off and back on again to clear the interrupt.

# Rules of Square D Network Addressing

## SY/MAX Point-to-Point Rules (Peer to Peer Communications)

- 1)	Any route addresses entered will be ignored.

- 2)	A COM port does not have a route address.

- 3)	A PLC does not have a route address (but it may have an Ethernet address).

- 4)	When you communicate from the COM port, Peer-to-Peer must be disabled on the PLC if there are no other peers.

## SY/LINK Net-to-Net Rules

- 1)	You cannot create a Bridge between a SY/LINK network and a SY/ENET network.

- 2)	While a Net-to-Net connection can be made between PLC on SY/NET and a PLC on SY/ENET, you cannot create a Bridge through this connection.  (For example, Figure 1 shows that the PLC Model 650 on the SY/ENET network (Net “C”) cannot be reached by any of the PLCs on Net “A” or Net “B”).

- 3)	The first route address on a SY/LINK card is always the COM port 0 address, even if only the RS-422 port is being used. For example, Figure 1 shows that to go from the PC on Net “A” to the Model 700 PLC on Net “B”, the route address would be 4,104,116, and not 104,116).

- 4)	Do not run the SY/LINK DDE Server and the Square D programming software at the same time through the same SY/LINK card.  Instead, either use two SY/LINK cards or a separate station for the programming software.

- 5)	The NIM address (that is, the thumbwheel switch) must be the same on both the Source and Destination NIMs.

- 6)	All devices must run at the same network speed and they all must recognize the same network size.

- 7)	You cannot use a SY/LINK card as a Bridge.

# The SY/ENET Network

The SY/ENET network is the Square D Local Area Network (LAN).  The SY/ENET network can support data rates of 500 Kbaud at distances of up to 2,500 feet, and data rates of 62.5 Kbaud at distances of up to 15,000 feet.  These data rates and distances can be increased by using a fiber-optic cable.  The SY/NET network must terminate with 78 Ohm resistors, as shown in Figure 1.

Here are some specifics you should be aware of when configuring the SY/ENET network:

- The SY/ENET network requires a proprietary Ethernet card in the PC that is made by Square D (or one made by ATI).

- The SY/ENET network runs on thin wire only.

- The network addressing can range from 00 to 99.

- Each SY/ENET address must be unique.

Important  If the address is not unique, it will cause the PLCs to hang.  If they do hang, restart them by turning the PLC power off, then back on.

- No routing is required if it is an Ethernet drop.

- The settings in the SF1610.DAT file for the Ethernet card must be properly defined.

Figure 1.  Example Square D Network Configuration

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editor: Mari Fujii;  Technical Publications Coordinator:  Sabrina Haag;  Director of  Technical Support: Sheila S. Tyler;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92718.  E-mail your questions or requests to techpub@wonderware.com.

There is also technical information on the Wonderware software products on the Wonderware Bulletin Board Service at (714) 727-0726, on the Wonderware CompuServe® forum (GO WONDER), and on the Comprehensive Support Knowledge Base CD.  Call Wonderware Technical Support at (714) 727-3299 for more information on the BBS, the Wonderware forum, or the Knowledge Base CD.

Copyright 1996 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

April 19, 1995  Number 13