Number  53	April 3, 1997

Configuring the Siemens SINEC H1 CP1413 for 
Windows NT  by Erik Oh

This Tech Note describes how to correctly configure the Siemens SINEC H1 CP1413 adapter card for Windows NT 3.51 and Windows NT 4.0 to run with the Wonderware® Siemens SINEC H1 CP1413 DDE Server for Windows NT.

# Procedure

1)	Install the SINEC H1 CP1413 adapter card in the computer by following the instructions in the Siemens hardware installation documentation provided with the adapter card.

- Install the Siemens TF-1413/Windows NT software program on your computer by following the instructions in the Siemens software installation documentation provided with the software program.  The directory C:\Sinec should be created, along with a program group and icon for the SINEC Setup program under the Windows NT Start menu.  The command line for the SINEC Setup program will be: C:\Sinec\Tools.Nt\Setupwnt.exe.

- The SINEC Setup program will automatically start up immediately after the installation to allow you to enter the configuration data.  Or, you can enter this program by clicking on its program icon.

- When the SINEC Setup program starts, you should see this dialog box:

- Note the version number of the SINEC Setup program and make sure that ir reads Version 1.36 or later.  Click the OK button to start the SINEC Setup program.

- 4)	In the SINEC Setup program window, highlight CP 1413 from the CP type list.  Select Configure new CP or Modify configured CP from the Edit menu as shown here:

- The SINEC Reconfiguration CP 1413 dialog box should appear:

- Delete any entries in the Compatible databases listbox (example: Sample.ldb).  Under the PC hardware parameter section, make sure that the Device name is listed as “CP_H1_1:” and enter the I/O Port address, the Interrupt level and the Dual-port-RAM address for the H1 CP1413 adapter card that was installed under step 1.

- Click the OK button.

- 5)	The following dialog box should appear:

- Click the OK button.  The following dialog box should appear:

- Click the Yes button if you want to save the configuration data and exit the SINEC Reconfiguration CP 1413 dialog box.  (Click the No button if you want to abandon the configuration data and exit the reconfiguration dialog box or click the Cancel button if you want to return to the reconfiguration dialog box to begin again.)

- You should see the following dialog box appear:

- Click the OK button to ackoowledge the message.

- 6)	After you have saved the CP 1413 configuration data, you should see the SINEC Setup program window reappear, as shown in step 4.

- Highlight the TF-1413/Windows NT entry in the Software Package listbox, then select Driver from the Edit menu.  Select Activate from the Driver menu’s drop down menu as shown on the next page

- Then, select Exit from the File menu to exit the SINEC Setup program.

- Shut down the Windows NT operating system and reboot the computer.

- 7)	The CP 1413 device driver should be running properly after the system reboots.  (Note that Windows NT may take longer to start up again because of the installed device driver.)

- Verify that the CP 1413 device driver was loaded and started up properly by one of two ways:

- Make sure that the Windows NT Event Viewer has no errors logged for the CP 1413 device driver when Windows NT started up.

Or

- Start up the SINEC Startup program, then highlight CP 1413 from the CP type list.  Select Diagnostic from the SINEC Startup program’s Edit menu.  Then select State from the Diagnostic menu’s drop down menu.

You should see the following SINEC Setup program window appear on the following page which lists the valid parameters for the CP 1413.

The above window indicates that the CP 1413 device driver is running properly.  If you see only one line listed in the window, then the driver is not running.  If this is the case, then you should review the previous steps and make sure that you have properly installed and configured the CP 1413 device driver.

Congratulations!  You have properly installed, configured and tested the SINEC H1 CP1413 adapter card and it is ready to be used with the H1 CP1413 DDE Server.

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Technical Publications Coordinator: Sabrina Haag;  Director of  Technical Support: Sheila S. Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

April 3, 1997  Number 53