Number  64	May 9, 1997

Configuring Modicon SA85/SA85-002 Cards, Bridge Multiplexer 85 and Bridge Plus 85  by Robert Acosta

This Tech Note describes how to configure the Modicon SA85/SA85-002 adapter cards, the Modicon Bridge Multiplexer 85 (BM85) and the Modicon Bridge Plus 85 (BP85).

# Configuring Modicon SA85/SA85-002 Adapter Cards

The Modicon SA85/SA85-002 adapter cards allow a computer to act as a master node and can enable a Modbus Plus DDE Server to communicate to nodes and slave devices on the Modbus Plus network.  The difference between the SA85 and SA85-002 adapter cards is that the SA85-002 adapter card contains dual ports for redundancy on the Modbus Plus network.  To configure the SA85/SA85-002 adapter cards, set the adapter jumper for Polled Mode and set two DIP switches: one that defines the network node address and one that sets the memory base address.

## Setting the DIP Switches for the Network Node Address

To define the node address for an SA85/SA85-002 adapter card, set the network address DIP switches on the card to the desired address.  The following diagrams show the location of the network address DIP switches for the SA85/SA85-002 adapter cards.

SA85 Adapter Card				                  SA85-002 Adapter Card

A switch is considered to be in position ‘1’ when it is set toward the numbers on the DIP switch. Likewise, a switch is considered to be in position ‘0’ when it is set away from the numbers on the DIP switch.  Use switches 1 through 6 to set the node address.  Note that switches 7 and 8 are not used.

The following diagram shows the numbered DIP switches and a combination of settings that can be used to set an SA85/SA85-002 adapter card node address between 1 and 64.

Note  Modicon recommends not setting the SA85/SA85-002 adapter cards to address 1 or 64.  Using address 1 could create confusion if a local default address of 1 is used at a controller node’s programming panel.  Address 64 should be reserved for network maintenance.

## Setting DIP Switches for the Memory Base Address

The SA85/SA85-002 adapter cards should use a memory area in the computer that does not conflict with other boards in the computer.  Use the memory base address switches to define the address for the memory area, as seen in the following diagrams:

SA85 Adapter Card				          SA85-002 Adapter Card

The following table shows the possible memory base configurations that can be set by these switches:

# Configuring the Bridge Multiplexer 85

A set of switches on the rear panel of the Bridge Multiplexer 85 (BM85) allow you to configure the serial ports and set the Modbus Plus node address.  The Bridge Multiplexer contains non-volatile memory that will store the port configurations after the unit is turned off.

- Switch 1 puts the Bridge Multiplexer into configuration mode or run mode;

- Switches 2 and 3 define which port on the Bridge Multiplexer will connect to the serial terminal program, such as the Windows Terminal;

- Switches 4 through 7 set the baud rate and parity mode to match the terminal emulation program settings.  Always use 8 data bits and 1 stop bit when communicating to the device;

- Switch 8 should be left in an upright position.

The following diagrams show the location of the switches on the rear panel and the settings you should use to configure the Bridge Multiplexer serial ports.  Make sure that the Bridge Multiplexer is turned off before you set the switches.

## Configuring the Serial Ports

To configure the serial ports, connect a terminal emulation program, such as Windows Terminal, to one of the Bridge Multiplexer ports.   The Bridge Multiplexer does not need to be connected the Modbus Plus Network.  Use a null modem cable to connect the serial port on the computer to the defined port on the Bridge Multiplexer.  The null modem cable could be a minimum pin-out which only uses three lines: transmit, receive and ground; or it could be a ‘full-handshake’ which uses all signals.

When the terminal emulation program has established communication with the Bridge Multiplexer, it will display a screen similar to the following:

MODICON MODBUS BRIDGE/MUX - Ver 1.01

Copyright (c) 1989 MODICON Inc., Industrial Automation Systems Group

MODBUS PORTS CONFIGURATION [V1]

[Modbus Plus Address = 64]

<COMMANDS>                                                     					[OPTIONS]

<P>PORT NUMBER#   	1          	 2           	3          	 4       	 [1, 2, 3, 4]

<T>Port Type      		slave       	slave       	slave       	slave     [m, s, n, x]

<N>Slave Dev Addr 		1           	1          	 1          	 1       	 [1 - 247]

<B>Baud Rate      		19200       	9600      	  19200      	 9600    [300 - 19200]

<S>Stop Bits      		1           	1          	 1           	1       	 [1, 2]

<R>Parity         		even        	even       	 even        	even      [n, o, e]

<M>Mode           		rtu         	rtu         	rtu         	rtu      	 [a, r]

<Y>Priority       		1           	2           	3           	4       	 [1 - 4]

<L>Link Timeout   		600        	 600         	600        	 600      [1 - 3000]

<F>Modem Booster  		-          		 -           	-          		 -       	 [y, n]

>>Valid Commands:[V1 V2 V3 V4 P T N B S R M Y L F]   Keys:[Enter Esc ?-help]<<

Active Port 1>>

After the terminal emulation program displays this screen, you may configure the Bridge Multiplexer serial ports.  (See the Modicon Modbus Plus Network BM85 Bridge Multiplexer User’s Guide or contact Modicon for any questions about configuring the Bridge Multiplexer or using the terminal emulation program.)  Once the serial ports are configured appropriately, run the Bridge Multiplexer to use the new settings.

Note  The Modbus Plus DDE Server can only communicate through a serial port that is configured as either a ‘Network’ or ‘Slave.’

## Configuring the Bridge Multiplexer Modbus Plus Address

Use switches 1 through 6 on the rear panel of the Bridge Multiplexer to set the Modbus Plus address.  Be sure not to use switches 7 and 8.  The following diagram and table illustrate the location of the switches and the switch settings that can be used to set the Modbus Plus address.

# Configuring the Bridge Plus 85

To assign the network addresses for the Bridge Plus 85 (BP85), use switches 1 through 6, located on the unit's rear panel.  Be sure not to use switches 7 and 8.  The following diagram and table illustrate the location of the network address switches and the switch settings for the addresses that you will assign to the Bridge Plus 85.

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Technical Publications Coordinator: Sabrina Haag;  Director of  Technical Support: Sheila S. Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.                                                 May 9, 1997  Number 64