Number  91	                                                                     January 30, 1998

Using HistData With InTouch and Excel by Daniela Tulbure

HistData is a utility program that comes with Wonderware® InTouch™.  It is used to retrieve data from the InTouch historical log files via DDE and then write the requested data to a .CSV file.  HistData cannot be used alone; another program is required in order to update HistData’s internal database items.  This Tech Note gives an example of how to use HistData with InTouch and Microsoft® Excel™.  In addition, common error messages and problems associated with HistData are presented with suggested solutions.  The appendix at the end of this Tech Note contains detailed information about the items that are in the HistData internal database.

# Using HistData With InTouch

1.  Start WindowMaker and select DDE Access Name from the Special  menu to create a new Access Name.  In the Add DDE Access Name dialog box, configure the Access Name with the settings shown below:

The DDEAccess name is user defined and can be up to 32 characters. The topic name is also user defined. The DDEApplication/Server Name must be HistData and the Advise all items option must be selected.

2.  Next, create the following DDE tags to generate one .CSV file that contains the data from the encrypted log files:

- Note  The HistData tags and the DDE Access Name  will be automatically created if you use the HistData wizard.  Just select the HistData wizard and place the icon on your window.  Double-click the icon and assign a Historical Trend tag (you can click the Suggest button).  Click OK to create the HistData tags.

## Tagname		Type			DDE Access Name		Item

HDWDbDir 		DdeMessage		Viewstream1			DbDir

HDWDataDir		DdeMessage		Viewstream1			DataDir

HDWDuration		DdeMessage		Viewstream1			Duration

HDWInterval		DdeMessage		Viewstream1			Interval

HDWStartDate	DdeMessage		Viewstream1			StartDate

HDWStartTime	DdeMessage		Viewstream1			StartTime

HDWFileName	DdeMessage		Viewstream1			FileName

HDWTags		DdeMessage		Viewstream1			Tags

HDWTags1		DdeMessage		Viewstream1			Tags1

HDWStatus		DdeDiscrete		Viewstream1			Status

HDWError		DdeMessage		Viewstream1			Error

HDWWriteFile	DdeInteger		Viewstream1			WriteFile

If you want to send the data not only to the .CSV file, but also to the item called Data so that it can be accessed from other applications, create the following two additional tags:

## Tagname		Type			DDE Access Name		Item

HDWSendData	DdeDiscrete		Viewstream1			SendData

HDWData		DdeMessage		Viewstream1			Data

- Note  If you create and use these tags and then request a lot of information you will get the error:  Too much data requested – shorten the duration or reduce the number of tags.

Here is an example of how a configured tag will look:

3.  After you have created the DDE tags, create a new window called HistData that looks similar to the following:

The # symbols are linked to a user input link.  For example,  the  # symbol below has a User Inputs/String linked to the tagname HDWDataDir.  The user inputs link will enable you to change the value of the tags during runtime.

The Status button below is linked to a fill color—discrete expression, based on the tag HDWStatus.

Here is the configuration for the Status button:

The Write File button below is linked to a fill color—discrete expression, based on the tag HDWWriteFile.

Here is the configuration for the Write File button:

The Initialize Data button below is linked to a Touch Pushbutton—Action script.  When pushed , the HistData items will be initialized with the desired values.  If  necessary, these values can also be changed during runtime by using the User Inputs Links.

Here is the configuration for the Initialize Data button:

The Write File button below is also linked to a Touch Pushbutton—Action script.  When clicked, the WriteFile button will generate the .CSV file.

Here is the configuration for the Write File button:

4.  After all the above items are configured and saved, start HistData and minimize it.  Next, start WindowViewer and open the HistData window.  Click the Initialize button, then make changes to the  HistData items if needed, and click the WriteFile button.

If the operation was successful, the value of Status will be ON and the color associated with the ON status will display.  If the operation was not successful, the value of Status will be OFF and the Error Message will display the cause of the failure.

# Using HistData with Excel

Excel macros can be written to interface with HistData.  Here is an example of a macro written with Excel 5.0VBA (same for Excel 7.0 or Excel 97):

Note that the data that is poked comes from a cell in the Excel spreadsheet1, called Sheet1.  Here is an example of  Sheet1 containing the data to be poked:

# Common Problems With HistData and How to Solve Them

##### Problem:  No CSV file is created and no errors are displayed.

Possible causes:

- HistData is not running

- The TAGS item does not list any tag that is checked for log data, such as:  HDWTags=”$Date,$Time”.  In this case you will get no errors, but the .CSV file will also not be created.

- The HDWWritefile is incorrectly defined.  Make sure the tag is a DDE Integer tag, the DDEAccess name is correct and the item is WriteFile.  Also make sure there is no scaling where MinEU=MinRaw and MaxEU=MaxRaw.

Problem:  The  .CSV file has no data for the requested tags but the Date and Time stamps are showing.

Possible causes:

- There are no records in the log files for the specified date and time.  You can trend the tags using the Historical Trend to see if there are any records showing.

- The tagname dictionary has been corrupted.  If the HistData items were initialized successfully (no errors were displayed by the Error item) but a corruption occurred in the tagname dictionary in the time between the initialization of the HistData items and the time you set the WriteFile item to 1, then it is possible that HistData could create a file with no data for the requested tags.

Suggestion:

Reinitialize the HistData items and perform the WriteFile again.  Monitor the error messages displayed by the Error item and also check the WWLogger for error messages.  If there is any problem with the tagname dictionary, an error should appear in the WWLogger, similar to the following:  Error for DDE HistData|Viewstream1!WriteFile : Poke was rejected by the server.  The Error HistData item should also display an error similar to the following:  could not find tagname.x’ or ‘DBDir invalid item’

Problem:  In my WWLogger I have the following message:  Error for DDE HistData|Viewstream1!WriteFile : Poke was rejected by the server
Possible causes:

This error will be posted in the WWLogger each time the creation of the .CSV file fails due to errors in assigning the values to the HistData items.  This error may also occur if you try to set the WriteFile item to 0 (its default value) or if you try to write to the error item.  For example, the following commands will post an error message in the WWLogger:  HDWWriteFile=0 or HDWError=”none”.

Problem:  The .CSV file has only one record when there should be many records.  For example, say that you requested data for 1 hour at 1/2 second intervals, yet the .CSV file has only one record.

Possible cause:

The interval item may have an invalid format, such as HDWinterval=500ms instead of HDWinterval=.5s.  The duration item may also have an invalid format, such as HDWDuration=1— (with no increment specified).

# Common HistData Error Messages With Suggested Solutions

Error Message:  Too much data requested – shorten the duration or reduce the number of tags

Solution:

This error occurs when you are using the SendData item and too much data is requested.  If the only purpose is to create a .CSV file with the data from the encrypted log files, then do not use SendData.

Error Message:  Could not open file C:\FILES1\HISTDATA.CSV

Possible cause:

The directory Files1 does not exist. Also, check the spelling of the path.

Error Message:  Could not open file C:\FILES\

Possible cause:

No CSV file was defined.

Error Message:  DATADIR item invalid

Possible cause:

The directory specified for the DataDir item does not exist.  Check the spelling.

Error Message:  STARTDATE item invalid

Possible cause:

Invalid format sent to the StartDate item.

Error Message:  No log files found

Possible cause:

There are no log files for the requested date in the path that is specified for the DataDir item.

Error Message:  Could not find tagname TAGX in database

Possible cause:

The requested tag (in this case, TAGX) does not exist in the tagname dictionary. Check the spelling of the tag.

Error Message:  Could not find tagname .x in: C:\IT6.0B\HISTEST

Possible cause:

The file tagname.x does not exist or it has been corrupted.

# Appendix

The following items are in the HistData database:

| ITEM | TYPE | DESCRIPTION |
| --- | --- | --- |
| DataDir | Message | Holds information about the path to the historical log files. |
| DBDir | Message | Holds information regarding the path to the InTouch tagname database (path to the Application directory). |
| StartDate | Message | Holds the date you want to start retrieving information. For InTouch 6.0b, the valid format is MM/DD/YY. For InTouch 5.6b, InTouch 6.0bSP1, and InTouch 7.0, the valid format can be either MM/DD/YY or DD-MM-YY, as long as the same format is used for the Windows operating system under Regional Settings in the Windows Control Panel (If a different format is used for Windows, an error message will appear.). |
| StartTime | Message | Holds the time you want to start to retrieve information. The valid format is HH:MM:SS. |
| Duration | Message | Holds the length of time for which data is to be retrieved. Duration can be expressed in weeks(w), days(d), hours(h), minutes(m), and seconds(s). Fractional values are also permitted, such as.5s for 500ms. |
| Interval | Message | Holds the length of time between samples. Can be expressed in weeks(w), days(d), hours(h), minutes(m), and seconds(s). Fractional values are also permitted, such as .25d for 6 hours. |

- Note  The maximum length of time allowed for Duration and Interval is 6 weeks. This applies to all requested types, days, seconds, etc.  For example, 42 is the maximum value for days (7 days x 6 weeks = 42).

| Tags | Message | Holds the list of tags requested. The “tags” string can hold 131 characters in WindowViewer and 255 characters in Excel. |
| --- | --- | --- |
| Tags1,Tags2, etc. | Message | In this case, more tags can be entered using these items. If a tagname needs additional tag text appended to it, a plus (+) sign is entered at the end of the string. For example: Tags=”$date,”Time,tag1,tag2,…tag20,+” Tags1=”tag21,tag22,….tag40,+” Tags2=”tag41,tag42” |
| Filename | Message | Holds the path to the .CSV file that will be created. |
| Error | Message | Holds a description of the last error. |
| PrintTagnames | Discrete | By default, this item is 1 and will cause HistData to print the tagnames on the first line of the .CSV file above the associated column of values. If the tagnames are not to be printed, this value should be set to 0 (zero). |
| SendData | Integer | Used to update the Data item ONLY. It does not perform any other operation. If SendData is used and the Duration and Interval parameters generate a response that is intended for the .CSV file that is >32K, an error will occur. You should not use SendData if a lot of information is requested. |
| Data | Message | Holds the requested data in a .CSV format. It can be used by other applications that want to Advise or Request data via DDE. |
| Status | Discrete | Displays the status of the last operation. A 1 indicates success and a 0 indicates that an error occurred. |
| Writefile | Integer | When set to 1, HistData will generate a .CSV file with the requested data. WriteFile is automatically reset to 0 when the file is written. |

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Director of  Technical Support: Sheila Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your publication questions or topic requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the Technical Services web page at http://www.wonderware.com/support/, the Wonderware Bulletin Board Service at (714) 727-0726, the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the Technical Services web page, the BBS, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1998 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.                                            January 30, 1998  Number 91